## Sheet1
S.No | Water Parameters | Units | WHO Limits | PAK-NEQS | Raw Water | Treated Water
Physical and Chemical Parameters | Physical | and Chemical | Parameters | * | * | *
1 | Appearance | - | Clear | Clear | Turbid | clear
2 | Temperature | °. | - | --- | 13 | 13
cost | Turbidity | NTU | 5 NTU | 5 NTU | 25 | 2.93
4 | pH | - | 6.5-8.5 | 6.5 - 8.5 | 7.32 | 7.15
5 | Alkalinity | mg/1 | 500 mg/1 | - | 218 | 184
6. | Hardness as CACO3 | mg/ 1 | 500 mg/l | < 500 mg/l | 236 | 194
7 | Conductance | uS/cm | 2000µS/cm | - | 596 | 570
8 | Sulphate | mg/ 1 | <400 mg/1 | ---- | - | -
9. | Calcium | mg/1 | 200 mg/l 150 | - | 50 | 46
10 | Magnesium | mg/ 1 | mg/l | - | - | -
11 | Total Dissolved Solids | mg/ 1 | 1000 mg/l | 1000 mg/1 | 2908 | 205
12 | Chlorides | mg/ 1 | 200 mg/1 | <250mg/l | 5 | 870
13 | Residual Chlorine | mg/ 1 | 0.5-1.5mg/l | 0.5-1.5mg/l | 0.0 | 0.7
456 | Sulfite | mg/1 | <10 mg/l | - | - | -
75 | Nitrite as NO2 | mg/1 | <1 mg/l | <3mg/l | NiL | NiL
· 16 | Ammonia as NH3 - N | mg/1 | 1.5 mg/l | - | NiL | NiL
17 | Iron as Fe | mg/1 | 0.3 mg/l | - | NiL | NiL
18 N8 | Dissolved Oxygen (DO) | mg/1 | 6 to10 mg/l | 6 to10 mg/l | 2.0 | 2.5
Bacteriological Parameters | * | Bacteriological | Parameters | * | * | *
19 | Total Coliform Count | Colonies/100ml | Nil/100 ml | Nil/100 ml | - | -
20 | Fecal Coliform Count | Colonies/100ml | Nil/100 ml | Nil/100 ml | 135/100ml | NiL/100ml
35 Toxic Substances 0.2 | -3-5 | Toxic Substances | 0.2 | * | * | *
21 | Arsenic as As | mg/ 1 | mg/1 | < 0.05 | - | -
22 | Cyanide as CN | mg/1 | 0.01 mg/l | <0.05 | - | -